## Cover and Project Info
METEOROLOGICAL MAST - PROCUREMENT QUALITY CHECKLIST
Lattice Structure ¦ Wind Resource Assessment ¦ India
Template Version 2.0 ¦ Prepared by: Wind Projects Engineering Team
PROJECT INFORMATION
Project Name | Rajasthan Wind Resource Assessment - Phase 1
Project Location | Jaisalmer District, Rajasthan, India
Client / Developer | Green Horizon Energy Pvt. Ltd.
EPC / Consultant | WindTech Engineering Solutions Pvt. Ltd.
Document Reference | GHEL-JSLM-MM-PRQ-001
Mast Height | 120 m (Lattice, Free-Standing)
No. of Masts | 2 Nos.
Site Coordinates | Lat: 27.0833 N ¦ Long: 70.9000 E
Terrain Category | Category II - Open Flat Terrain (IS 875 Part 3)
Wind Zone | Wind Zone V - Basic Wind Speed 50 m/s (IS 875)
Procurement Stage | RFQ / Technical Bid Evaluation
Expected Delivery | 16 weeks from Purchase Order
Installation Start | Q3 2025
Monitoring Duration | Minimum 12 months (target 24 months)
Prepared By | Arun Sharma - Lead Wind Resource Engineer
Reviewed By | Priya Nair - Senior Structural Engineer
Date of Issue | 2025-06-01
Document Status | DRAFT FOR REVIEW
DOCUMENT INDEX
Sheet | Title | Content Summary | Status
Sheet 1 | Cover and Project Info | Project metadata and document control | Included
Sheet 2 | Vendor Qualification | Pre-qualification criteria and scoring | Included
Sheet 3 | Mast Structure Tech Spec | Structural design, material, loads | Included
Sheet 4 | Foundation and Civil | Foundation design and civil requirements | Included
Sheet 5 | Fabrication and QA-QC | Shop fabrication checklist and inspection | Included
Sheet 6 | Surface Protection | Galvanizing, coating, corrosion protection | Included
Sheet 7 | Erection and Safety | Field erection, safety requirements | Included
Sheet 8 | Instrumentation | Sensors, data logger, cabling | Included
Sheet 9 | Documentation | Drawings, certifications, reports | Included
Sheet 10 | Commercial Terms | Warranty, delivery, payment, LD | Included
Sheet 11 | Bid Evaluation Matrix | Weighted scoring for vendor comparison | Included
ABBREVIATIONS
Abbreviation | Full Form
IS | Indian Standard
IEC | International Electrotechnical Commission
MET | Meteorological
WRA | Wind Resource Assessment
NDA | Non-Disclosure Agreement
QA | Quality Assurance
QC | Quality Control
MTC | Mill Test Certificate
FAT | Factory Acceptance Test
SAT | Site Acceptance Test
RFQ | Request for Quotation
PO | Purchase Order
LD | Liquidated Damages
HAT | Hub Height Anemometry Tower
BOM | Bill of Materials
PPE | Personal Protective Equipment

## Vendor Qualification
VENDOR PRE-QUALIFICATION CHECKLIST - MET MAST (LATTICE STRUCTURE)
Project: Rajasthan WRA Ph-1 ¦ Client: Green Horizon Energy Pvt. Ltd. ¦ Doc: GHEL-JSLM-MM-PRQ-001
PURPOSE: This sheet captures the minimum qualification criteria a vendor must meet before receiving the RFQ. All Mandatory items must be satisfied. Score Preferred items for ranking.
# | Qualification Criterion | Requirement / Benchmark | Vendor Response / Evidence | Mandatory / Preferred | Compliance (Y/N/Partial)
A. COMPANY PROFILE AND EXPERIENCE
A1 | Years in business - lattice tower / telecom / met mast fabrication | Minimum 10 years in structural steel fabrication |  | Mandatory
A2 | Number of met masts / lattice towers fabricated and supplied | Minimum 15 met masts (>=80 m height) in last 5 years |  | Mandatory
A3 | Experience with projects in high wind zone / desert terrain | At least 3 projects in Wind Zone IV or V (IS 875 Part 3) |  | Preferred
A4 | Experience supplying to renewable energy developers | Wind energy developers or IPPs as past clients |  | Preferred
A5 | In-house structural engineering team | At least 2 qualified structural engineers (B.E./B.Tech Civil/Structural) |  | Mandatory
B. CERTIFICATIONS AND QUALITY SYSTEM
B1 | ISO 9001:2015 - Quality Management System | Valid, scope covering structural steel fabrication |  | Mandatory
B2 | ISO 3834 - Welding quality requirements | ISO 3834-2 or 3834-3 preferred |  | Preferred
B3 | IS 2062 / IS 808 material procurement compliance | Steel sourced from SAIL/TATA/JSPL or equivalent |  | Mandatory
B4 | Third-party inspection empanelment | Must accept Bureau Veritas / TUV / DNV inspection |  | Mandatory
B5 | CE Marking or IEC compliance for tower structure | IEC 61400-1 structural loads reference preferred |  | Preferred
B6 | Compliance with Factories Act and labour laws | Valid factory licence, ESI/PF registration |  | Mandatory
C. MANUFACTURING FACILITY
C1 | In-house fabrication workshop area | Minimum 5,000 sq.m covered fabrication area |  | Mandatory
C2 | CNC / plasma / laser cutting machines | Minimum 1 CNC plasma/laser cutting machine |  | Preferred
C3 | Drilling and punching machines for angle / plate | Radial drill / CNC drill, capacity >= 32 mm dia |  | Mandatory
C4 | Overhead crane capacity | Minimum 10-tonne EOT crane in assembly bay |  | Mandatory
C5 | Hot-dip galvanizing facility (in-house or tie-up) | BS EN ISO 1461 / IS 4759 compliant; tie-up acceptable |  | Mandatory
C6 | Welding equipment and certified welders | MIG/MAG/SMAW; welders certified per IS 7310 |  | Mandatory
C7 | NDT testing capability | UT / MPI / DPT in-house or third-party empanelled |  | Mandatory
C8 | Pre-assembly / trial erection area | Adequate yard for pre-assembly of full mast sections |  | Preferred
C9 | Material traceability system | Heat-number based traceability from mill to dispatch |  | Mandatory
D. DESIGN CAPABILITY
D1 | In-house structural analysis software | STAAD.Pro / SAP2000 / Tekla or equivalent |  | Mandatory
D2 | Signed and stamped structural design report | Licensed Structural Engineer (Member of IStructE / IE(I)) |  | Mandatory
D3 | Foundation design capability or sub-consultant | Geotechnical input integration; spread / pile foundation design |  | Preferred
D4 | Wind load calculation per IS 875 Part 3 / IEC 61400-1 | Design basis document referencing applicable codes |  | Mandatory
D5 | Fatigue analysis capability | S-N curve based fatigue life assessment for lattice members |  | Preferred
D6 | Deflection / tilt analysis | Maximum allowable tip deflection criteria stated |  | Preferred
E. FINANCIAL AND COMMERCIAL STANDING
E1 | Annual turnover | Minimum INR 10 Crore (avg. last 3 financial years) |  | Mandatory
E2 | Net worth positive | Positive net worth in latest audited balance sheet |  | Mandatory
E3 | Bank solvency / credit line | Bank solvency letter equivalent to contract value |  | Mandatory
E4 | No litigation / blacklisting | Self-declaration not blacklisted by any GoI body |  | Mandatory
E5 | Ability to provide Performance Bank Guarantee | 10% of PO value; validity PO duration + 6 months |  | Mandatory
F. HSE - HEALTH, SAFETY AND ENVIRONMENT
F1 | Dedicated HSE officer in factory | Full-time qualified safety officer |  | Mandatory
F2 | Lost Time Injury frequency (LTIF) rate | LTIF < 1.0 per million man-hours (last 3 years) |  | Preferred
F3 | HSE plan for field erection | Site-specific HSE plan to be submitted before erection |  | Mandatory
F4 | PPE compliance | Mandatory PPE for all workers during fabrication and erection |  | Mandatory

## Mast Structure Tech Spec
METEOROLOGICAL MAST - STRUCTURAL TECHNICAL SPECIFICATION CHECKLIST
Project: Rajasthan WRA Ph-1 ¦ Mast Height: 120 m ¦ Type: Self-Supporting Lattice ¦ Wind Zone: V
Ref | Parameter / Question to Vendor | Client Requirement / Benchmark | Vendor Proposed Value / Response | Applicable Code / Standard | Importance | Compliance (Y/N/Partial)
1. GENERAL MAST CONFIGURATION
1.1 | What is the proposed mast type? | Self-supporting lattice steel tower; no guy wires; free-standing |  |  | Critical
1.2 | What is the total hub/sensor height? | 120 m above finished ground level (FGL); confirm with survey benchmark |  |  | Critical
1.3 | What is the base width (footprint) of the lattice at foundation level? | Minimum 10-12% of total height (>=12 m base width for 120 m); confirm calculation |  |  | Critical
1.4 | What are the proposed section heights and number of sections? | Sections <=12 m for transportability; state number and flange splice locations |  |  | High
1.5 | What is the design wind speed used for structural design? | V_b = 50 m/s (Zone V); K1=1.08 (50yr return); K2, K3 as per terrain |  |  | Critical
1.6 | Has gust factor / dynamic analysis been performed? | Gust factor method or dynamic analysis; resonance check required |  |  | High
1.7 | What is the maximum allowable tip deflection? | <= H/150 under design wind load (<= 800 mm for 120 m) |  |  | High
1.8 | What is the design life of the mast structure? | Minimum 25 years; fatigue loading considered for repeating wind cycles |  |  | Critical
1.9 | What is the maximum mast tilt / plumb tolerance after installation? | <= 1:500 of height (<= 240 mm lateral lean) measured at top |  |  | Critical
1.10 | Is a pre-erection trial assembly planned at factory? | Yes - full mast trial assembly mandatory before dispatch; photos + survey report |  |  | High
2. STRUCTURAL STEEL - MATERIAL SPECIFICATION
2.1 | What steel grade is proposed for main leg members (chord)? | IS 2062 E350 BR (FU min 490 MPa, FY min 350 MPa); Charpy impact >=27J @ 0 deg C |  |  | Critical
2.2 | What steel grade for bracing / diagonal members? | IS 2062 E250 A minimum; E350 preferred for higher-load bracings |  |  | High
2.3 | What section profiles are used for legs, bracings, and platforms? | Legs: rolled steel equal/unequal angles or SHS/RHS; Bracings: angles or rods; state BOM |  |  | High
2.4 | How is material traceability maintained from mill to final product? | Heat number stamping / colour coding; Mill Test Certificates (MTC) for every heat |  |  | Critical
2.5 | What is the carbon equivalent (CE) of the proposed steel? | CE <= 0.43% for weldability (IS 2062 E350); confirm weld procedure qualification |  |  | High
2.6 | Is the steel sourced from primary (integrated) steel plants? | SAIL / TATA Steel / JSW / JSPL or equivalent; secondary/re-rolled NOT acceptable |  |  | Critical
2.7 | What is the plate/section thickness range for leg and gusset plates? | State min and max thickness; ensure thickness >= 8 mm for main legs at base |  |  | High
2.8 | Are all bolts, nuts, and washers hot-dip galvanized high-tensile? | Grade 8.8 bolts HDG per IS 1367 Part 13; property class 8 nuts; hardened washers |  |  | Critical
2.9 | Are flanged bolted joints or welded splices used for section joints? | Flanged bolted joints preferred for on-site assembly; HSFG bolts at flanges |  |  | High
2.10 | What is the proposed bolt diameter and pitch at main splice flanges? | State bolt size (M24/M27/M30), grade, pitch, edge distance; preload torque values |  |  | High
3. STRUCTURAL DESIGN LOADS
3.1 | What are the dead loads considered? | Provide load summary: self-weight, instrument load, ice/snow if applicable, cable load |  |  | Critical
3.2 | What wind loads are applied at each section height? | Show wind pressure distribution (kN/m2) at 10 m intervals; solidity ratio of lattice faces |  |  | Critical
3.3 | Are instrument drag loads included in structural design? | Anemometer, wind vane, boom arm drag; minimum 0.5 kN horizontal load per boom level |  |  | High
3.4 | What is the design seismic zone and seismic coefficient used? | Rajasthan - Zone III; seismic load per IS 1893 Part 1 |  |  | High
3.5 | Is a combined wind + seismic load combination checked? | Per IS 800 load combinations; governing load case identified |  |  | High
3.6 | What factor of safety (FOS) is applied to structural members? | FOS >= 1.5 on yield; member utilisation ratio <= 0.90 under ultimate load |  |  | Critical
3.7 | Is fatigue life assessed for high-cycle wind loading? | IEC 61400-1 fatigue load classes; S-N curves for welded joints; design life >= 25 yr |  |  | High
3.8 | Are guy wire attachment loads included (if applicable)? | N/A for self-supporting; if temporary guys used during erection, loads must be stated |  |  | Medium
4. SECTION GEOMETRY AND PLATFORM DETAILS
4.1 | What are the cross-arm / boom arm specifications? | Boom length: min 2.0 m from mast face; state boom tube O.D., wall thickness, material |  |  | Critical
4.2 | How many instrument platforms / service platforms are provided? | Min 2 intermediate access platforms (at ~40 m and ~80 m); top instrument platform |  |  | High
4.3 | What are the platform dimensions and load rating? | Min 0.6 m width; load rating >= 2.5 kN/m2 live load; anti-slip grating |  |  | High
4.4 | What fall protection / safety cage / rest platforms are provided? | Full height safety ladder with safety cage >= 2.5 m or fall-arrest rail (EN 353-1) |  |  | Critical
4.5 | What is the ladder rung spacing and side rail dimensions? | Rung spacing: 300 mm; side rail width: min 300 mm; galvanized steel throughout |  |  | High
4.6 | How are cable and conduit runs managed on the mast? | Dedicated cable tray / conduit brackets at max 2 m spacing; earthing cable route |  |  | High
4.7 | Are aviation warning lights and mounting provisions required? | Yes - aviation obstruction light provision per DGCA / AAI requirements at top and mid height |  |  | Critical
4.8 | What is the top plate configuration for instrument mounting? | Instrument mounting ring / top plate with pre-drilled holes for anemometer and vane booms |  |  | High
5. EARTHING AND LIGHTNING PROTECTION
5.1 | Is a dedicated earthing and lightning protection system provided with the mast? | Yes - fully designed earthing per IS 3043; lightning protection per IS/IEC 62305 |  |  | Critical
5.2 | What is the proposed earthing electrode system? | Minimum 4 nos. copper-bonded earth rods (3 m x 17 mm); ring electrode around foundation |  |  | Critical
5.3 | What is the target earth resistance value? | <= 5 Ohm (measured after installation); <= 10 Ohm in rocky terrain with chemical treatment |  |  | Critical
5.4 | Are surge protection devices (SPDs) supplied for instruments? | SPDs at data logger cabinet and at each signal/power cable entry - Class II SPD minimum |  |  | Critical
5.5 | Is the earthing system compatible with data logger cabinet bonding? | All metallic parts bonded; equipotential bonding bar in data logger enclosure |  |  | High
5.6 | What type of lightning finial / air terminal is proposed? | Franklin rod type; min 1.5 m above highest instrument; Cu or Al alloy |  |  | High
6. PAINTING AND MARKING
6.1 | What aviation marking colour scheme is proposed? | Red and white alternate bands (600 mm) per DGCA CAR; top section red |  |  | Critical
6.2 | What is the mast identification marking / nameplate? | SS nameplate welded at base: project name, mast ID, height, year of fabrication, vendor name |  |  | High
6.3 | Are height interval markers provided on the mast? | Yes - height markers every 10 m for instrument level identification |  |  | Medium

## Foundation and Civil
FOUNDATION AND CIVIL WORKS - SPECIFICATION CHECKLIST
Project: Rajasthan WRA Ph-1 ¦ Soil: Silty Sand / Sandy Soil ¦ Foundation: Spread Footing
Ref | Parameter / Question | Requirement / Benchmark | Vendor Response | Standard | Importance | Compliance
1. GEOTECHNICAL INVESTIGATION
1.1 | Has a site-specific geotechnical investigation report been provided? | BH/DCPT/SPT to min 1.5x foundation depth or 6 m; by licensed geo firm |  |  | Critical
1.2 | What is the allowable bearing capacity (ABC) at foundation depth? | ABC >= 100 kN/m2 at proposed founding level; SBC from plate load test preferred |  |  | Critical
1.3 | What is the groundwater table depth? | Min 1.5 m below foundation bottom; if shallow, waterproofing and buoyancy check needed |  |  | High
1.4 | Is soil liquefaction assessment performed (seismic zone III)? | SPT-N >= 15 or liquefaction assessment as per IS 1893 Annex F |  |  | High
1.5 | What is the soil corrosivity classification? | pH, sulphate, chloride content of soil; if aggressive, use SRPC cement and coated rebars |  |  | High
2. FOUNDATION DESIGN
2.1 | What foundation type is proposed? | Spread (isolated pad) footing for each leg; raft or pile if soil is poor; justify with analysis |  |  | Critical
2.2 | What is the design bearing pressure under combined loads? | Factored bearing pressure <= 0.9 x ABC; uplift check under wind/seismic |  |  | Critical
2.3 | What concrete grade is specified for foundation? | M30 minimum for footings; M25 for PCC blinding layer; RCC design as per IS 456 |  |  | Critical
2.4 | What is the foundation reinforcement specification? | Fe 500D TMT bars (IS 1786); clear cover >= 75 mm (soil face); 50 mm (top face) |  |  | Critical
2.5 | How are anchor bolts / base plates designed and anchored? | HSFG anchor bolts M36 minimum; embedded depth >= 20x bolt dia; with anchor plate and hook |  |  | Critical
2.6 | Is foundation design report stamped by licensed structural engineer? | Yes - design calculations signed by licensed engineer (IE(I) membership) + drawings stamped |  |  | Critical
2.7 | What is the foundation excavation plan and backfill specification? | Compacted backfill in 150 mm layers; Proctor density >= 95%; no organic material |  |  | High
2.8 | Is a concrete cube testing plan included? | Min 3 cubes per pour; 7-day and 28-day tests; report to be submitted to client |  |  | Critical
2.9 | Is a foundation settlement monitoring plan included? | Survey benchmarks; settlement reading at 0, 3, 6, 12 months after erection |  |  | High
3. CIVIL ANCILLARY WORKS
3.1 | What is the access road specification to mast location? | All-weather gravel road; min 4 m width; capable of carrying 10T loaded truck |  |  | High
3.2 | What is the equipment laydown / erection pad specification? | Min 20 m x 20 m compacted area near mast; capable of supporting crane outrigger loads |  |  | High
3.3 | Is a perimeter security fence provided around the mast base? | Min 1.8 m chain link fence with barbed wire top; lockable gate; warning signage in local language |  |  | Critical
3.4 | What is the data logger enclosure foundation / mounting specification? | RCC plinth (0.3 m above FGL); anti-vibration pads; bolted to plinth |  |  | High
3.5 | Are cable trenches / conduits provided from mast to data logger? | PVC conduit >= 50 mm ID buried >= 0.6 m; drawstring provided; marked with warning tape |  |  | High
3.6 | Is site levelling / grading included in scope? | 3 m radius around each mast leg graded and compacted; drainage channel if needed |  |  | Medium

## Fabrication and QA-QC
FABRICATION QUALITY ASSURANCE AND QUALITY CONTROL (QA/QC) CHECKLIST
Project: Rajasthan WRA Ph-1 ¦ Third-Party Inspection: Bureau Veritas India ¦ Stage: Shop Fabrication
Ref | Inspection / QC Item | Acceptance Criterion | Inspection Record / Document | Inspection Stage | Hold (H) / Witness (W) / Review (R) | Compliance
1. INCOMING MATERIAL INSPECTION
1.1 | Verification of steel mill test certificates (MTC) | Chemical composition and mechanical properties comply with IS 2062; heat number tallies | MTC file (per heat number) | On receipt of material | H
1.2 | Dimensional check of incoming sections (angle, plate, rod) | Thickness/width within IS 1852 tolerance; cross-check with approved BOM | Material receiving report | On receipt | W
1.3 | Visual inspection for laminations, cracks, surface defects | Zero laminations; no cracks; minor mill scale acceptable; heavy rust rejected | Visual inspection record | On receipt | W
1.4 | Verification of bolt, nut, washer certificates | Grade 8.8 property class; IS 1367 compliant; lot-wise test cert | Bolt/nut MTC | On receipt | H
1.5 | Welder qualification record (WQR) verification | All welders qualified per IS 7310 / IS 817; records current (< 3 years) | WQR register | Before fabrication start | H
2. CUT, DRILL AND FIT-UP INSPECTION
2.1 | Dimensional accuracy of cut members | Length tolerance +/-2 mm; angle of cut +/-0.5 deg; check with calibrated steel tape | Cutting inspection report | After cutting | W
2.2 | Hole diameter, pitch, and edge distance | Hole dia = bolt dia + 2 mm clearance; pitch and edge distance per IS 800 Cl. 10.4 | Drilling inspection report | After drilling | W
2.3 | Fit-up inspection before welding | Root gap <= 2 mm; bevel angle per WPS; misalignment <= 2 mm | Fit-up inspection report | Before welding | H
2.4 | Weld joint geometry check | Throat thickness, leg length per WPS; visual check weld profile | Weld visual report | During / after welding | W
2.5 | Weld seam NDT - UT / MPI / DPT | All full-penetration butt welds: UT per IS 4260; fillet welds: MPI or DPT 10% sampling | NDT report (third-party) | After welding | H
2.6 | Distortion and straightness check after welding | Bow <= L/1000; angular distortion <= 1 deg; twist <= 1 mm/m | Dimensional inspection report | After welding | W
3. ASSEMBLY AND SUB-ASSEMBLY INSPECTION
3.1 | Match-marking of bolt holes in mating flanges | All bolt holes align without reaming; max 3 holes may need minor dressing | Assembly fit-up report | During assembly | W
3.2 | Flange flatness (mating splice flanges) | Flatness <= 1 mm over 1 m; checked with straight edge + feeler gauge | Flange inspection report | Before dispatch | H
3.3 | Member length and diagonal dimension check | +/-3 mm on member length; diagonal tolerance +/-5 mm across full section face | Dimensional report | Assembly | W
3.4 | Platform grating assembly and weld inspection | Anti-slip grating welded / clipped; weld quality visual; load test platform if feasible | Platform inspection report | After assembly | W
3.5 | Ladder / safety cage assembly check | Rung spacing 300 mm +/- 5 mm; cage ring diameter correct; alignment straight | Ladder inspection report | After assembly | W
3.6 | Trial erection / pre-assembly at factory | All sections erected to full height or representative sub-assembly; photos recorded | Trial erection report + photos | Before dispatch | H
4. SURFACE TREATMENT INSPECTION
4.1 | Surface preparation (blast cleaning) before galvanizing / painting | Sa 2.5 (near white blast) per ISO 8501-1; checked immediately before treatment | Surface prep report | Before treatment | W
4.2 | Hot-dip galvanizing thickness measurement | Local coating >= 45 micron; mean >= 55 micron (IS 4759 / BS EN ISO 1461); DFT gauge | GI inspection report | After galvanizing | H
4.3 | Galvanizing visual - runs, bare spots, lumpiness | No bare spots >2 mm2; runs and drips dressed; no cracking of GI coat | Visual GI report | After galvanizing | W
4.4 | Aviation colour paint DFT (over galvanized surface) | Primer: epoxy zinc phosphate >= 50 micron; Topcoat: polyurethane >= 60 micron DFT | Paint DFT report | After painting | W
4.5 | Bolt threads protection before dispatch | All threads greased and protected with polyethylene sleeve / thread protector | Packaging inspection | Before dispatch | R
5. PRE-DISPATCH INSPECTION (PDI)
5.1 | Final dimensional check of all sections | Refer drawings; all critical dims confirmed; no missing holes | PDI report | Before loading | H
5.2 | Quantity verification against BOM / packing list | 100% count; part numbers match drawing; no loose items without marking | BOM vs. packing list | Before dispatch | H
5.3 | Documentation completeness check | Design report, GA drawings, BOM, MTC, GI certs, NDT reports, WQR, test certs | Document checklist | Before dispatch | H
5.4 | Packing and transport protection | Heavy members on wooden dunnage; fragile items wrapped; bolts in sealed bags labeled | Packing inspection report | Before dispatch | W
5.5 | Dispatch clearance certificate | Issued jointly by vendor QC and client/TPI representative | Dispatch clearance cert | Before loading | H
LEGEND FOR INSPECTION HOLD POINTS
H - HOLD POINT | Work CANNOT proceed without client/TPI witness and sign-off. Inspector must be present.
W - WITNESS POINT | Client/TPI to be notified 48 hrs in advance. Work may proceed if inspector absent after notice.
R - REVIEW POINT | Submit documentation for review. No physical presence required.

## Surface Protection
SURFACE PROTECTION - GALVANIZING, COATING AND CORROSION CHECKLIST
Project: Rajasthan WRA Ph-1 ¦ Environment: Arid/Desert ¦ Corrosivity Category: C3 per ISO 9223
Ref | Item / Question | Requirement | Vendor Response | Standard | Importance | Compliance
1. HOT-DIP GALVANIZING (HDG)
1.1 | Which standard governs the galvanizing process? | IS 4759:1996 (HDG on structural steel) and/or BS EN ISO 1461:2009 |  |  | Critical
1.2 | What is the minimum zinc coating thickness (local and mean)? | Local: >= 45 micron; Mean: >= 55 micron (steel > 6 mm thick) |  |  | Critical
1.3 | What pre-treatment process is used before galvanizing? | Degreasing -> acid pickling (HCl) -> rinsing -> fluxing -> drying |  |  | High
1.4 | What is the zinc bath composition? | Zinc purity >= 98.5%; temperature 445-455 deg C; dross control maintained |  |  | High
1.5 | How are internal surfaces of hollow sections galvanized? | Vent holes provided; internal surface also galvanized; confirm hole positions on drawings |  |  | High
1.6 | How is repair of GI coating carried out (if damage during transport)? | Cold galvanizing compound (zinc-rich paint >95% Zn in DFM) per IS 4759 Cl. 7; min 3 coats |  |  | High
1.7 | Who performs coating thickness inspection (DFT gauge)? | Vendor QC + independent TPI (BV/DNV/TUV) - calibrated elcometer/DFT gauge |  |  | Critical
1.8 | What documentation is provided for galvanizing? | GI certificate per batch: steel weight galvanized, coating thickness readings, date |  |  | Critical
2. ADDITIONAL PAINT / COATING SYSTEM (AVIATION MARKING)
2.1 | What is the paint system specified over galvanized surface? | Sweep blast -> Epoxy zinc phosphate primer 50 micron DFT -> Mid-coat epoxy 40 micron -> Polyurethane topcoat 60 micron DFT |  |  | High
2.2 | What aviation colours are used and what is the gloss level? | International Orange (Red: RAL 3020) and White (RAL 9010); Semi-gloss (Gloss 40-60) |  |  | Critical
2.3 | What is the minimum expected paint system durability? | Medium durability (M) per ISO 12944 - 5 to 15 years to first maintenance |  |  | High
2.4 | How is inter-coat adhesion verified? | Cross-cut adhesion test per ISO 2409; pull-off adhesion >= 3 MPa per ISO 4624 |  |  | High
2.5 | What touch-up procedure is used for paint damage at site? | Feathering, clean with solvent, apply matching topcoat; provide touch-up kit with mast |  |  | Medium
3. CORROSION PROTECTION OF BOLTS AND HARDWARE
3.1 | What surface protection is applied to structural bolts and nuts? | Hot-dip galvanized M24+ bolts per IS 1367 Part 13; zinc thickness >= 40 micron |  |  | Critical
3.2 | Are stainless steel bolts used in instrument mounting areas? | SS 316 bolts for all instrument boom mounting, anemometer brackets, sensor mounts |  |  | High
3.3 | What anti-seize compound is used on bolt threads? | Molybdenum disulphide (MoS2) grease or copper-based anti-seize on all structural bolts |  |  | High
3.4 | Are spring washers + flat washers used on all bolted connections? | Yes - lock washer or Nordlock washer to prevent self-loosening under dynamic wind load |  |  | High
3.5 | What protection is provided for anchor bolts below ground? | Coal tar epoxy coating >= 300 micron on anchor bolt embedded section; petrolatum tape wrap |  |  | Critical
4. CATHODIC / SACRIFICIAL PROTECTION (IF APPLICABLE)
4.1 | Are sacrificial anodes proposed for below-ground structural steel? | Zinc or magnesium sacrificial anodes bolted to foundation steelwork if soil is aggressive |  |  | Medium
4.2 | What is the soil corrosivity test result and corrosion risk classification? | Soil resistivity, pH, sulphate, chloride - classify per ISO 9223 / IS recommendations |  |  | High

## Erection and Safety
ERECTION, INSTALLATION AND SAFETY CHECKLIST
Project: Rajasthan WRA Ph-1 ¦ Erection Method: Mobile Crane ¦ Site: Jaisalmer, Rajasthan
Ref | Erection / Safety Item | Requirement | Vendor / Erection Agency Response | Standard | Importance | Compliance
1. PRE-ERECTION PLANNING
1.1 | Is a detailed erection methodology statement (EMS) provided? | Step-by-step erection sequence; crane positions; section lifting scheme; rigging plan |  |  | Critical
1.2 | What crane capacity is proposed for erection? | Confirm crane capacity sufficient for heaviest lift at maximum radius; crane chart appended |  |  | Critical
1.3 | Is a site-specific risk assessment / Job Safety Analysis (JSA) prepared? | JSA for each critical task (crane lift, high-work, electrical); reviewed by HSE officer |  |  | Critical
1.4 | Are ground bearing pressure calculations provided for crane outriggers? | Crane outrigger loads; ground bearing capacity check; matting if required |  |  | High
1.5 | What is the erection team qualification and experience? | Erection supervisor: min 5 years lattice tower erection experience; riggers certified |  |  | High
1.6 | Is a Permit-to-Work (PTW) system in place? | PTW for height work, crane operation, electrical connections; daily toolbox talk |  |  | Critical
2. FOUNDATION AND BASE PLATE INSTALLATION
2.1 | How are anchor bolt positions set out and checked? | Survey instrument (total station / theodolite); check position and level before concrete pour |  |  | Critical
2.2 | What is the process for checking anchor bolt plumb and projection? | Templates used during concrete pour; projection tolerance +/-5 mm; plumb <= 1 mm/m |  |  | Critical
2.3 | What grout specification is used under base plates? | Non-shrink cementitious grout (Fosroc / MBT / equivalent); compressive strength >= 60 MPa |  |  | Critical
2.4 | How is the mast base plumb verified after grouting? | Theodolite check in two orthogonal directions; plumb <= 1:1000 at base |  |  | Critical
3. SECTION-BY-SECTION ERECTION
3.1 | What lifting technique is used for each mast section? | Four-point lift with spreader beam; certified slings; SWL marked on all lifting gear |  |  | Critical
3.2 | How are mast sections aligned and bolted? | Drift pins used for hole alignment; no reaming without approval; torque wrench used |  |  | Critical
3.3 | What is the bolt tightening procedure and torque values? | Snug tight then full tightening (turn-of-nut method or calibrated torque wrench) |  |  | Critical
3.4 | Is a progressive plumb check performed during erection? | Check plumb every 3 sections; correct any deviation before proceeding |  |  | Critical
3.5 | How are temporary guys / bracing used during erection (if any)? | Temporary guys designed for erection wind speed; anchor positions surveyed; released in sequence |  |  | High
3.6 | What is the maximum wind speed permitted during erection? | Stop erection if site wind speed > 10 m/s; anemometer on site during erection |  |  | Critical
4. EARTHING AND LIGHTNING INSTALLATION
4.1 | How are earth electrodes installed and tested? | Drive rods using portable driver; fill pit with bentonite/coke; test resistance before backfill |  |  | Critical
4.2 | How are earth conductors connected to mast structure? | Exothermic weld (cadweld) or compression lugs; no painted/GI surface at connection points |  |  | Critical
4.3 | What test equipment is used for earth resistance measurement? | Fall-of-potential method; calibrated digital earth tester (Kyoritsu / Fluke) |  |  | Critical
5. POST-ERECTION CHECKS AND COMMISSIONING
5.1 | What are the final verticality / plumb acceptance criteria? | Top-of-mast lateral deviation <= H/500 (<= 240 mm for 120 m) in any direction |  |  | Critical
5.2 | Is a final bolt torque check performed after erection? | 100% check on all critical bolted connections (splice flanges, base plate); record torque values |  |  | Critical
5.3 | Is a mast visual inspection report produced post-erection? | Inspection checklist: plumb, bolt tightness, GI damage, platform security, ladder continuity |  |  | Critical
5.4 | Is a handover / as-built documentation package provided? | As-built drawings, erection report, plumb survey, bolt torque records, earth test report |  |  | Critical
5.5 | Is a site acceptance test (SAT) conducted before instrument commissioning? | Structural SAT: plumb, security, earthing; Instrument SAT: sensor operation, data flow |  |  | Critical
6. WORKER SAFETY AND HSE
6.1 | What fall protection system is used during erection? | Full-body harness (EN 361); double lanyard; fall-arrest devices on safety rail |  |  | Critical
6.2 | Is a rescue plan for height emergencies in place? | Rescue plan documented; rescue kit at mast base; first-aider on site |  |  | Critical
6.3 | Are all workers covered under ESIC / insurance during erection? | Workmen's compensation policy; ESIC coverage; contractor's all-risk (CAR) insurance |  |  | Critical
6.4 | What is the daily toolbox talk and incident reporting procedure? | Daily TBT before work; near-miss / incident report within 24 hours to client HSE |  |  | High
6.5 | Is a visitor management and site induction procedure in place? | Site induction mandatory before entering erection zone; visitor log maintained |  |  | High

## Instrumentation
INSTRUMENTATION, DATA LOGGER AND CABLING - SPECIFICATION CHECKLIST
Project: Rajasthan WRA Ph-1 ¦ Standard: IEC 61400-12-1 ¦ Data Logger: NRG Systems / Ammonit / Kintech
Ref | Instrument / Parameter | Specification Required | Proposed by Vendor | Standard | Importance | Compliance
1. WIND SPEED MEASUREMENT (ANEMOMETERS)
1.1 | Type of anemometer | Class 1 cup anemometer (IEC 61400-12-1); Thies First Class Advanced / NRG #40C or equivalent |  |  | Critical
1.2 | Measurement heights | Min at: hub height (120m), 2/3 hub (80m), 1/3 hub (40m); redundant sensor at top level |  |  | Critical
1.3 | Measurement range | 0-75 m/s; starting threshold <= 0.5 m/s |  |  | Critical
1.4 | Accuracy / uncertainty | +/- 2% at 12 m/s; calibration certificate traceable to national standard |  |  | Critical
1.5 | Calibration certificate | MEASNET accredited calibration; calibration date < 12 months from installation |  |  | Critical
1.6 | Boom orientation and mounting | Boom direction: prevailing wind; offset from mast >= 2x mast face width; SS316 mounting |  |  | Critical
1.7 | Heated anemometers (if icing risk) | Not mandatory for Rajasthan desert; confirm not required based on site temperature history |  |  | Medium
2. WIND DIRECTION MEASUREMENT (WIND VANES)
2.1 | Type of wind vane | Potentiometric or optical encoder wind vane; Thies / NRG 200P or equivalent |  |  | Critical
2.2 | Measurement heights | Min at: top level (120m) and mid level (80m); mounted perpendicular to anemometer boom |  |  | Critical
2.3 | Measurement range and accuracy | 0-360 deg (with <=10 deg dead band); accuracy +/-3 deg; resolution <=1 deg |  |  | Critical
2.4 | Dead band orientation | Dead band pointing toward prevailing wind direction to minimise data loss |  |  | High
3. TEMPERATURE AND PRESSURE SENSORS
3.1 | Air temperature sensor type and housing | Pt100 or Pt1000 RTD; naturally ventilated radiation shield; Stevenson screen or equivalent |  |  | High
3.2 | Temperature measurement heights | At 2 m and at 120 m minimum; aspirated shield preferred at top level |  |  | High
3.3 | Temperature measurement range and accuracy | Range: -20 deg C to +65 deg C; Accuracy: +/-0.3 deg C |  |  | High
3.4 | Barometric pressure sensor | Capacitive or piezoelectric; range 800-1100 hPa; accuracy +/-0.5 hPa; at base level |  |  | High
4. OTHER SENSORS
4.1 | Relative humidity sensor | Capacitive RH sensor +/-3% accuracy; range 0-100% RH; co-located with temperature |  |  | Medium
4.2 | Precipitation / rain gauge | Tipping bucket rain gauge (0.2 mm resolution) for data quality flagging |  |  | Medium
4.3 | Ice detection sensor (if required) | Not required for Rajasthan; confirm based on T_min records |  |  | Low
4.4 | Vertical wind component (3D sonic anemometer) | Optional: 3D ultrasonic anemometer at hub height for turbulence intensity measurement |  |  | Medium
5. DATA LOGGER AND ACQUISITION SYSTEM
5.1 | Data logger type and manufacturer | IEC 61400-12-1 compliant; NRG Symphonie / Ammonit Meteo-40 / Kintech KP or equivalent |  |  | Critical
5.2 | Logging intervals | 10-minute statistics (mean, std dev, max, min) mandatory; 1-second raw data optional |  |  | Critical
5.3 | Data storage capacity | Onboard memory >= 1 year of 10-min data; removable CF/SD card + USB port |  |  | Critical
5.4 | Remote data transfer | GPRS / 4G SIM-based data transfer; daily upload to cloud server; SMS alarm capability |  |  | Critical
5.5 | Data security and encryption | Encrypted data transmission (HTTPS / VPN); tamper-evident logger enclosure |  |  | High
5.6 | Clock accuracy and time synchronisation | GPS-synchronized clock; accuracy +/- 1 second; auto-sync on upload |  |  | Critical
5.7 | Input channels | Min 16 analog + 8 digital channels; expandable; state channel allocation in bid |  |  | High
5.8 | Operating temperature range of data logger | -40 deg C to +70 deg C; internally heated enclosure if temperature goes below -10 deg C |  |  | High
5.9 | Power supply | Solar panel (40 W min) + sealed gel battery (100 Ah min); backup 3-5 days without sun |  |  | Critical
5.10 | Enclosure IP rating | IP 65 minimum for data logger enclosure; outdoor-rated, lockable, ventilated |  |  | Critical
6. CABLING AND SIGNAL INTEGRITY
6.1 | What type of signal cable is used from sensors to logger? | Shielded twisted pair (STP) cable; PE outer sheath; UV resistant; rated -40 to +80 deg C |  |  | Critical
6.2 | How are cables protected on the mast structure? | PVC conduit or SS316 cable tray secured at <= 2 m intervals; UV-stable cable ties |  |  | High
6.3 | Are cable lengths within sensor specification limits? | Resistance of cable run within logger channel specifications; voltage drop calculated |  |  | High
6.4 | Is shielding earthed at one end only? | Cable shield earthed at logger end only to avoid ground loops |  |  | High
6.5 | Are all cable entries to logger sealed against moisture ingress? | Cable glands (IP68) on all entries; unused entries blanked |  |  | Critical
7. DATA QUALITY AND REPORTING
7.1 | What data recovery rate is targeted? | >= 95% data recovery (per channel) over the monitoring period |  |  | Critical
7.2 | What data quality flags / filters are applied? | Out-of-range, icing, sensor failure, tower shadow flags per IEC 61400-12-1 |  |  | Critical
7.3 | How frequently is the mast inspected and calibrated? | 6-monthly site visit: sensor check, re-orientation, calibration verification, logger check |  |  | High
7.4 | What reporting format is used for wind data? | Standard .txt / .csv (IEC compliant); compatible with WindPRO / WAsP / OpenWind |  |  | Critical
7.5 | Is a mast commissioning report and sensor configuration sheet provided? | Yes - signed commissioning report: serial nos., boom directions, heights, channel allocations |  |  | Critical

## Documentation
DOCUMENTATION AND DELIVERABLE REQUIREMENTS
Project: Rajasthan WRA Ph-1 ¦ All documents in English; drawings in AutoCAD + PDF
Ref | Document / Deliverable | Format / Standard | Submission Timing | Copies Required | Mandatory? | Received
A. DESIGN AND ENGINEERING DOCUMENTS
A1 | Structural design calculation report (signed by licensed SE) | PDF; stamped by IE(I) member; includes load summary, member checks, deflection, fatigue | With technical bid | 2 hard + soft | Mandatory
A2 | Foundation design calculation report | PDF; includes geotechnical input, bearing capacity, rebar design, anchor bolt design | With technical bid | 2 hard + soft | Mandatory
A3 | General arrangement (GA) drawings - mast elevation, section views, top plan | AutoCAD .dwg + PDF; scale 1:50 or 1:100; all dimensions, material callouts | With technical bid | 2 sets + soft | Mandatory
A4 | Foundation layout and reinforcement drawings | AutoCAD .dwg + PDF; anchor bolt layout, rebar schedule | Within 2 weeks of PO | Soft + 2 hard | Mandatory
A5 | Erection drawing and sequence diagram | PDF; section assembly sequence, crane positions, rigging details | 4 weeks before erection | Soft + 2 hard | Mandatory
A6 | Earthing and lightning protection scheme drawing | Single line diagram + layout; component schedule | With technical bid | Soft | Mandatory
A7 | Instrumentation layout drawing (boom locations, cable routing) | AutoCAD + PDF; heights, boom angles, sensor positions, cable routes | With instrumentation bid | Soft + 1 hard | Mandatory
A8 | Fatigue analysis report | S-N curve method; design life confirmation >= 25 years | With technical bid | Soft | Preferred
B. MATERIAL CERTIFICATES
B1 | Mill Test Certificates (MTC) for all structural steel | Per IS 2062 format; chemical + mechanical; heat number referenced to BOM | Before fabrication / with shipment | Originals | Mandatory
B2 | MTC for anchor bolts, nuts, washers | IS 1367 grade; lot-wise certificates | Before fabrication | Originals | Mandatory
B3 | Galvanizing inspection certificate (per batch) | IS 4759 / ISO 1461 format; DFT readings; GI plant name, date, batch | Before dispatch | Originals | Mandatory
B4 | Paint inspection record (DFT readings) | Each member; min 5 readings; primer + finish coat DFT | Before dispatch | Soft + 1 hard | Mandatory
B5 | NDT reports (UT / MPI / DPT) | Third-party inspector signed; heat-referenced; pass/fail status per joint | Before dispatch | Originals | Mandatory
B6 | Sensor / instrument calibration certificates | MEASNET accredited; individual serial-number-based | With instrumentation delivery | Originals | Mandatory
B7 | Data logger configuration sheet | Channel allocation, scaling factors, serial numbers, firmware version | At commissioning | Soft + 1 hard | Mandatory
C. QA/QC AND INSPECTION RECORDS
C1 | Inspection Test Plan (ITP) - signed by vendor + client/TPI | PDF; all hold/witness/review points; acceptance criteria; responsible parties | 2 weeks before fabrication start | Soft + 1 hard | Mandatory
C2 | Welder Qualification Records (WQR) | IS 7310 format; welder ID, process, position, test date, result | Before fabrication start | Soft | Mandatory
C3 | Dimensional inspection reports (cutting, drilling, assembly) | Per ITP; vendor QC sign-off; deviations noted with disposition | At each inspection stage | Soft | Mandatory
C4 | Trial erection / pre-assembly report with photographs | All sections erected; theodolite survey; deviation record; min 20 photographs | Before dispatch | Soft | Mandatory
C5 | Pre-dispatch inspection (PDI) report signed by client/TPI | Checklist format; hold point sign-off; quantity verification | Before dispatch | Soft + 1 hard | Mandatory
C6 | Factory Acceptance Test (FAT) report - instrumentation | All sensors and logger tested on bench; results vs. spec; signed | Before instrument dispatch | Soft | Mandatory
D. ERECTION AND COMMISSIONING RECORDS
D1 | Erection completion report | Sequence of erection; dates; crew; crane details; deviations; sign-off | Within 1 week of erection completion | Soft + 1 hard | Mandatory
D2 | Plumb / verticality survey report (post-erection) | Total station survey; deviation in X and Y at each section height; vs acceptance criteria | Within 3 days of erection | Soft + 1 hard | Mandatory
D3 | Bolt torque inspection record (post-erection) | Torque values for all critical joints; 100% check at splices | Within 1 week of erection | Soft | Mandatory
D4 | Earthing system test report | Earth resistance measurement; method (fall of potential); test equipment calibration cert | Before commissioning | Soft + 1 hard | Mandatory
D5 | Instrument commissioning / SAT report | Sensor operational check; boom direction; heights confirmed; data logger live test | At commissioning | Soft + 1 hard | Mandatory
D6 | As-built drawings | AutoCAD + PDF; updated from IFC drawings; any site deviations marked | Within 4 weeks of commissioning | Soft + 1 hard | Mandatory
D7 | Operation and Maintenance (O&M) manual for mast and instruments | Maintenance schedule; inspection checklist; sensor replacement guide; safety instructions | At commissioning | Soft + 1 hard | Mandatory
E. COMMERCIAL AND LEGAL DOCUMENTS
E1 | Performance Bank Guarantee (PBG) | 10% of PO value; unconditional; from scheduled bank; validity = PO duration + 6 months | Within 15 days of PO | Original | Mandatory
E2 | Insurance certificates (CAR, workmen's compensation) | CAR for full PO value; WCA for all workers; copies before site mobilization | Before site mobilization | Copies | Mandatory
E3 | Warranty letter / certificate | Minimum 3 years for structure; 1 year for instruments; defects liability clause | At delivery | Original | Mandatory
E4 | DGCA height clearance application support | Vendor to provide mast height, coordinates for DGCA NOC application by client | Before installation | Soft | Mandatory

## Commercial Terms
COMMERCIAL TERMS, WARRANTIES AND CONTRACTUAL REQUIREMENTS
Project: Rajasthan WRA Ph-1 ¦ Currency: INR ¦ Incoterms: DDP Site
Ref | Commercial Clause | Client Requirement | Vendor Offered Terms | Remarks | Priority | Agreed?
1. PRICING AND SCOPE OF SUPPLY
1.1 | What is the scope of supply - structure only or complete turnkey? | Preferred: Turnkey (supply, transport, erection, commissioning, 1st year O&M) |  |  | Confirm included/excluded items
1.2 | Is the price firm or subject to escalation? | Firm price for entire contract duration; no escalation for steel / labour |  |  | Client preference
1.3 | What are the payment milestone terms? | 10% advance on PO; 30% on drawing approval; 40% on dispatch; 15% on commissioning; 5% on DLP end |  |  | Client standard terms
1.4 | What taxes and duties are included in the price? | GST as applicable; HSN code for lattice mast structure to be confirmed; no hidden costs |  |  | GST Act 2017
1.5 | Is a detailed BoQ / BoM attached to the bid? | Yes - itemized BoQ with unit rates for structure, hardware, instruments, civil, erection |  |  | RFQ requirement
2. DELIVERY AND LOGISTICS
2.1 | What is the guaranteed delivery period? | Structure: 14 weeks from PO; Instruments: 8 weeks from PO |  |  | Client programme
2.2 | What is the delivery basis (Incoterms)? | DDP (Delivered Duty Paid) - delivered to site, Jaisalmer, Rajasthan |  |  | Incoterms 2020
2.3 | Is special transport / over-dimensional consignment (ODC) arranged? | Vendor responsible for all transport permits (ODC), escort, police clearance |  |  | Client requirement
2.4 | What is the packing standard for transport? | Wooden cradles for long members; polythene wrap on threaded ends; section-wise color coding |  |  | Client requirement
2.5 | What is the breakage / damage risk in transit responsibility? | Marine/transit insurance by vendor; replacement of damaged parts at vendor's cost |  |  | Commercial terms
3. LIQUIDATED DAMAGES (LD)
3.1 | What is the LD rate for delay in delivery? | 0.5% of PO value per week of delay; maximum 5% of PO value |  |  | Client standard
3.2 | What is the LD rate for delay in commissioning? | 0.5% per week; max 5% of commissioning milestone value |  |  | Client standard
3.3 | What is the LD rate for performance (data recovery < 95%)? | Proportional deduction from monthly O&M fee; re-inspection at vendor's cost |  |  | Client requirement
4. WARRANTY AND DEFECT LIABILITY
4.1 | What is the warranty period for mast structure? | Minimum 3 years from commissioning; free repair/replacement of structural defects |  |  | Client requirement
4.2 | What is the warranty period for instruments and data logger? | Minimum 1 year from commissioning; manufacturer's warranty passthrough |  |  | Client requirement
4.3 | What is the Defects Liability Period (DLP)? | 12 months from commissioning; 5% retention released at end of DLP |  |  | Client standard
4.4 | What is the vendor's on-call response time for critical failures? | Critical (data loss, mast damage): 48-hour response; Non-critical: 7 days |  |  | Client requirement
4.5 | Is a spare parts list and pricing provided? | Yes - mandatory list: sensors, booms, bolts, cable, logger battery, GI repair kit |  |  | Client requirement
5. INSURANCE AND INDEMNITY
5.1 | Is contractor's all-risk (CAR) insurance mandatory? | Yes - insured value = PO value; valid from site mobilization to commissioning |  |  | Client requirement
5.2 | Is third-party liability insurance required? | Yes - minimum INR 1 Crore per occurrence; vendor to name client as additional insured |  |  | Client requirement
5.3 | Is vendor responsible for any damage to public / private property? | Yes - full indemnity clause; vendor liable for third-party claims from their work |  |  | Contract clause
6. INTELLECTUAL PROPERTY AND CONFIDENTIALITY
6.1 | Are design drawings and reports confidential to this project? | Yes - NDA to be signed; drawings not to be reused for other projects without consent |  |  | NDA / Contract
6.2 | Who retains IP of the mast structural design? | Client retains right to use for this project; vendor retains design IP for other use |  |  | Contract clause
7. DISPUTE RESOLUTION
7.1 | What is the governing law and jurisdiction? | Laws of India; jurisdiction - courts of Jaipur / Mumbai (as agreed) |  |  | Contract
7.2 | Is arbitration preferred for disputes? | Arbitration per Arbitration and Conciliation Act 1996; seat: Jaipur; ICADR rules |  |  | Arbitration Act 1996

## Bid Evaluation Matrix
TECHNICAL BID EVALUATION MATRIX - MET MAST (LATTICE STRUCTURE)
Project: Rajasthan WRA Ph-1 ¦ Evaluation: 70% Technical / 30% Commercial ¦ Min Technical Score: 65%
Scoring: 0 = Not Compliant ¦ 1 = Partially Compliant ¦ 2 = Mostly Compliant ¦ 3 = Fully Compliant
Ref | Evaluation Criterion | Max Score | Vendor A (Ahmedabad) | Vendor B (Pune) | Vendor C (Chennai) | Remarks
SECTION 1: COMPANY QUALIFICATION (Weight: 15%)
1.1 | Years of experience in lattice tower / met mast fabrication | 5
1.2 | Number of met masts >=80 m supplied in last 5 years | 5
1.3 | ISO 9001 and welding quality certifications | 5
1.4 | Financial strength (turnover, net worth) | 5
1.5 | HSE record and HSE management system | 5
SECTION 2: MANUFACTURING FACILITY (Weight: 15%)
2.1 | Workshop area and equipment capability | 5
2.2 | In-house galvanizing or accredited tie-up | 5
2.3 | NDT capability (in-house / third-party) | 5
2.4 | Trial erection facility | 5
2.5 | Material traceability system | 5
SECTION 3: STRUCTURAL DESIGN (Weight: 25%)
3.1 | Design wind speed and IS 875 Part 3 compliance | 5
3.2 | Completeness of structural calculation report | 5
3.3 | Deflection and tilt criteria compliance | 5
3.4 | Foundation design adequacy | 5
3.5 | Fatigue analysis provided | 5
3.6 | Seismic load consideration (IS 1893) | 5
3.7 | Base width / stability ratio | 5
3.8 | Lightning protection and earthing design | 5
3.9 | Drawing quality and completeness | 5
3.10 | Erection methodology statement quality | 5
SECTION 4: MATERIAL AND SURFACE PROTECTION (Weight: 15%)
4.1 | Steel grade and source (primary mill) | 5
4.2 | Bolt grade and specification | 5
4.3 | Galvanizing specification (IS 4759 / ISO 1461) | 5
4.4 | Paint system for aviation marking | 5
4.5 | Corrosion protection below ground | 5
SECTION 5: INSTRUMENTATION (Weight: 15%)
5.1 | Anemometer class and MEASNET calibration | 5
5.2 | Data logger compliance (IEC 61400-12-1) | 5
5.3 | Communication and remote data transfer | 5
5.4 | Solar power supply adequacy | 5
5.5 | Data quality management and reporting | 5
SECTION 6: DELIVERY AND COMMERCIAL (Weight: 15%)
6.1 | Delivery period (structure and instruments) | 5
6.2 | Warranty terms (structure 3 yr, instruments 1 yr) | 5
6.3 | Price competitiveness (normalised to L1) | 5
6.4 | LD and performance guarantees | 5
6.5 | Past client references and feedback | 5
TOTAL MAXIMUM SCORE |  | 175 | SUM | SUM | SUM | SUM
SCORING GUIDE
Score 0 | Not Compliant - No evidence provided; requirement not met
Score 1 | Partially Compliant - Some evidence but gaps; partially meets requirement
Score 2 | Mostly Compliant - Meets most requirements; minor gaps noted
Score 3 | Fully Compliant - Complete evidence; fully meets or exceeds requirement